Hurst Feed Water System “Oxy-miser” Dual Tank (5,000pph – 200,000pph)

- Furnish a pressurized, spray type deaerating boiler feed water system, Hurst Oxy-Miser, model DOM-       -       -      , rated for       pounds per hour.    The deaerating system shall be guaranteed to provide for oxygen removal to not more than 0.005 cc/liter in the boiler feed water at all flow rates from 5% to 100% of outlet capacity.  The system shall operate at 5 to 7 psig.  The surge tank shall receive the returned condensate and supplement with make up water to provide for the dearating tank’s water requirements.  The dual tank design incorporates both the dearerator and the surge tank in one common shell, divided by a dished head between the two.  The dearating vessel shall be constructed for 50 psig as per the requirements of Section VIII of the ASME Code and registered with the National Board of Boiler and Pressure Vessel Inspectors.  The surge tank portion is not pressurized, and is vented to atmosphere.

- Make-up water shall be fed to the deaerator through spring operated, stainless steel spray nozzles to provide for complete and thorough atomization of the water in the steam bath.  Access to the steam scrubber section and the spray nozzles shall be provided for. Undisolved oxygen is vented to the atmosphere through an automatic vent valve.

- The deaerator shall be factory piped and wired with the following components.

- Water level control is to be of the electric modulating type using a McDonnell & Miller 93-7B proportioning control, or approved equal.  (Or, water level control is to be of the pneumatic type).  The level control shall send a proportioning signal to the make-up valve to maintain accurate water level in the tank.

- Provide a modulating feed water valve, Worcester or approved equal with a 3-valve by-pass arrangement.

- Provide a steam pressure reducing valve, Spence or approved equal, for reducing the inlet steam pressure from ___ psig to 5 psig.  Provide for a steam inlet strainer for installation up stream of the PRV.  The PRV and the strainer are to be shipped loose for field installation.

- Provide a water level gauge glass assembly that provides for visual indication of the tank water level.

- Provide for high water and low water level alarms.

- Provide a safety relief valve set at 50 psig and sized for the capacity of dearerator rating.

- Provide a tank thermometer and tank pressure gauge.

- Provide a vacuum breaker.

- Provide a sacrificial magnesium anode for cathodic protection against corrosion.  Internal tank linings are not acceptable.

- Provide a stainless steel ball check type chemical feed quill for injection of chemicals in the stored water.

- Provide an overflow drainer of the float trap type, sized to relieve the full capacity of the deaerator.

- Provide factory insulation and jacketing.  (Use our specs here).

- Provide a structural steel support stand using steel legs with minimum height to provide for the NPSHR of the pumps selected.  Provide for a steel base for pump supports.

- Provide a 12” x 16” manhole

- The surge tank shall be factory piped and wired with the following components.

- Water level control is to be of the electric modulating type using a McDonnell & Miller 93-7B proportioning control, or approved equal.  (Or, water level control is to be of the pneumatic type.)  The level control shall send a proportioning signal to the make-up valve to maintain accurate water level in the tank.

- Provide a modulating feed water valve, Worcester or approved equal with a 3-valve by-pass arrangement.

- Provide a water level gauge glass assembly that provides for visual indication of the tank water level.

- Provide for high water and low water level alarms.

- Provide a tank thermometer.

- Provide a sacrificial magnesium anode for cathodic protection against corrosion.  Internal tank linings are not acceptable.

- Provide two (2) vent connections for field installation of air vent lines.

- Provide factory insulation and jacketing.  (Use our specs here).

- Provide a structural steel support stand using steel legs with minimum height to provide for the NPSHR of the pumps selected.  Provide for a steel base for pump supports.

- Provide       boiler feed water pumps of the centrifugal type. Each pump shall be rated at       gpm with a discharge pressure of       psig. Provide two (2) condensater transfer pumps to pump water from the surge tank to the dearerator’s make-up inlet.  Each pump shall re rated

at       gpm with a discharge pressure of       psig. Electrical supply shall be       / 60 /      , with 3450 rpm, (ODP, or TEFC) motors.  (Optional, specify high efficiency motors.)  Pump seals shall be rated for 250 degrees F. Provide individual pump suction piping including a strainer with removable and cleanable basket, and a gate type shut off valve.  Pumps shall operate as on/off type and controlled by the respective boiler’s water level controls. (Or, pumps shall be continous run type to maintain boiler’s water level control automatically through the boiler’s proportioning water level control. Provide for pump discharge orifice for field installation of a recirculation line for minimum pump flow.)

(Optional:  Provide for each pump a discharge check valve with stainless steel spring and a liquid filled discharge pressure gauge.)

- Provide a factory wired NEMA 1 control panel enclosure, UL Listed and including Allen-Bradley pump motor starters and heater, circuit breakers, pump selector switches, and control panel lights for annunciation of pump operation and for high and low water level alarms.  Provide an electric alarm bell with silencing switch to alarm on high or low water levels.  The control panel shall be factory mounted on the support stand.

- The complete factory skid mounted and piped system may be “knocked” down for shipping purposes.  The contractor shall install the deaerating feed water system as indicated on the project drawings.

Hurst Boiler & Welding Co., Inc.  www.hurstboiler.com